MAINE PUBLIC DRINKING WATER

SOURCE WATER ASSESSMENT PROGRAM

SOUTHWEST HARBOR WATER DEPARTMENT

LONG POND WATERSHED

MARCH 2003

prepared for

Source Water Assessment Program

Drinking Water Program

Maine Department of Human Services

prepared by

Drumlin Environmental, LLC

Portland, Maine

MAINE PUBLIC DRINKING WATER

SOURCE WATER ASSESSMENT PROGRAM

SOUTHWEST HARBOR WATER DEPARTMENT

LONG POND WATERSHED

MARCH 2003

prepared for

Source Water Assessment Program

Drinking Water Program

Maine Department of Human Services

11 State House Station

Augusta, Maine  04333

prepared by

Drumlin Environmental, LLC

15 Franklin Street, P. O. Box 392

Portland, Maine 04112-0392

(207) 771-5546

MAINE PUBLIC DRINKING WATER

SOURCE WATER ASSESSMENT PROGRAM

SOUTHWEST HARBOR WATER DEPARTMENT

LONG POND WATERSHED

TABLE OF CONTENTS

Section      Title                                                                                                            Page No.

|  | EXECUTIVE SUMMARY | ii |
| --- | --- | --- |
| 1.0 | INTRODUCTION | 1 |
| 2.0 | WATER SUPPLY SOURCE | 1 |
|  | 2.1 Description | 1 |
|  | 2.2 Land Use | 2 |
| 3.0 | INVENTORY OF POTENTIAL WATER QUALITY CONCERNS | 3 |
|  | 3.1 Background | 3 |
|  | 3.2 Source Sensitivity to Land Use | 4 |
| 4.0 | # ASSESSMENT OF LONG POND | 5 |
|  | 4.1 Watershed | 5 |
|  | 4.2 Shoreland | 6 |
|  | 4.3 Intake | 7 |
| 5.0 | SWAP RANKING AND RECOMMENDATIONS | 8 |
|  | 5.1 Ranking of Susceptibility | 8 |
|  | 5.2 Recommendations | 9 |
|  | Table 1 - Long Pond Supply | 2 |
|  | Table 2 - Sources of SWAP Information | 4 |
|  | Table 3 - Long Pond Surface Water Assessment | 8 |
|  | Figure 1 - Public Water Supply and Surrounding Watershed | End |
|  | Figure 2 - Land Under Protective Ownership | End |
|  | ## Figure 3 - Multi-Resolution Land Characterization | End |
|  | Figure 4 - Potential Erodible Soils | End |
|  | Appendix A - SWAP Assessment Guidelines | End |

# SOUTHWEST HARBOR WATER DEPARTMENT

# LONG POND WATERSHED

# EXECUTIVE SUMMARY

The Southwest Harbor Water Department provides drinking water from Long Pond to approximately 2,200 customers in Southwest Harbor.  Long Pond is between 1,500 and 5,500 feet wide and more than three miles long.  Long Pond is approximately 931 acres in size, with an average depth of approximately 33 feet and a maximum depth of over 110 feet.  The outlet to the pond is located near its northern end and the water supply intake is located at the southern end of the pond.  Runoff and groundwater feed the pond from a 4,305-acre watershed that lies in the towns of Southwest Harbor and Mount Desert.  The watershed is forested with mixed deciduous and evergreen timber.  Wetlands occupy approximately five percent of the watershed area and developed land occupies approximately one percent of the watershed.

The southern and western parts of the watershed lie within Acadia National Park, which is managed for the US Government by the National Park Service.  The mandate of the National Park Service is to manage its land in its natural state with minimal human impact.  Land in the northern and eastern parts of the watershed is privately owned.  Zoning restricts future development to lots of two acres or more.  Current land uses include moderate- to high-density seasonal homes on the northern shore of the pond and low-density seasonal homes on the eastern shore.

The Park Service maintains a boat launch at the south end of Long Pond, near the intake.  The Town of Mount Desert maintains a boat launch at the north end of the pond.  Water contact activities (e.g., swimming, wading, etc.) are prohibited in the southern end of the pond, within one mile of the intake.  Other recreational uses, including fishing and boating, are permitted in all parts of the pond.  Ice fishing is permitted in the winter, with vehicles permitted on the ice in Mount Desert, but not in Southwest Harbor.

The Water Department intake is located at the southern end of the pond approximately 10 feet below the surface.  The pond is approximately 80 feet deep at the intake.  The Water Department and Park Service have posted signs on the shoreline identifying the water supply and listing the swimming restriction.  However, the intake is not marked on the pond.  Available Long Pond water quality data classify the pond as oligotrophic, with high clarity (7 to 10 meters secchi disk) and low chlorophyll-a (1 to 3 ppb).

Based on the undeveloped nature of the watershed near the intake, the high water quality and the protective ownership and management of the watershed, the overall susceptibility of the Long Pond water supply is considered to be low.

MAINE PUBLIC DRINKING WATER

SOURCE WATER ASSESSMENT PROGRAM

SOUTHWEST HARBOR WATER DEPARTMENT

LONG POND WATERSHED

1.0    INTRODUCTION

The operation of public water systems in Maine is governed by the federal Safe Drinking Water Act (SDWA), which was first passed in the 1970s and later amended in 1986 and 1996.   The federal government delegated authority for enforcing the SDWA to the state under the Maine Department of Human Services (DHS) Drinking Water Program (DWP).   In 1998, the Source Water Protection Section was established in the DWP to implement the Maine Public Drinking Water Source Water Assessment Program (SWAP).   The SWAP process is being conducted through a cooperative effort between the DWP staff, Southwest Harbor Water Department (Water Department) staff and Drumlin Environmental, LLC (Drumlin), the environmental consulting firm contracted through DHS to provide technical assistance for the project.

The purpose of the SWAP evaluation for the Water Department is to assess the susceptibility of its Long Pond drinking water supply (PWSID  91490) to potential threats of contamination.   The long-term goal is to protect the water supply source.   To do this, the SWAP process has compiled information to assist the Water Department in future planning that will help to control potential threats to the water quality of Long Pond.

This Report describes the SWAP for the Southwest Harbor Water Department and is organized as follows:

- Section 2.0  summarizes the physical characteristics of the water supply at Long Pond;

- Section 3.0  describes the variety of conditions and activities that could pose a threat to water quality;

- Section 4.0  provides an assessment of the threats within the Long Pond watershed; and,

- Section 5.0  ranks the susceptibility of the water quality at Long Pond and provides recommendations for future protection of water quality.

2.0   WATER SUPPLY SOURCE

2.1   Description

The Water Department draws its supply from the south end of Long Pond located in the Town of Southwest Harbor on Mount Desert Island.  The northern half of Long Pond is located in the Town of Mount Desert.  The Long Pond watershed is depicted in Figure 1.  The components and description of the Water Department source are presented below in Table 1.

# TABLE  1

# LONG POND SUPPLY

| # Category | # Description |
| --- | --- |
| Water System Name: | Southwest Harbor Water Department |
| Surface Water Source(s): | Long Pond |
| Water System Type: | Non-transient, community system |
| Watershed Location: | Southwest Harbor and Mount Desert |
| Source Surface Water Area: | 936 Acres |
| Source Watershed Area: | 4,305 Acres |
| Average/Maximum Depths (estimated): | 33 ft average; 112 ft maximum |
| Water Volume in Storage: | Undetermined |
| Population Served (customers): | Services: 600 (seasonal and year-round) Population: 2,280 |
| Type of Treatment: | Hypochlorate |
| Filtration: | Pressure Filtration |
| Estimated Daily Water Use: | 250,000 GPD average; 600,000 GPD peak use |

The Water Department intake is positioned at the extreme south end of Long Pond.  The intake is located approximately 10 feet below the water surface in water that is approximately 80 feet deep.  Signs on the shore identify the presence of the water intake, but the intake is not marked with buoys on the pond.

2.2   Land Use

The southern portion of the Long Pond watershed is located within the Town of Southwest Harbor.  The majority of the watershed land in Southwest Harbor lies within the boundaries of Acadia National Park, which is owned by the US Government.  The northern portion of the Long Pond watershed is located within the Town of Mount Desert.  Most of the land in Mount Desert along the western side of Long Pond is also in Acadia National Park.  It is the policy of the National Park Service, which manages Acadia National Park, to “manage natural resources to maintain, restore and perpetuate their inherent integrity; and to allow for natural processes to evolve minimally influenced by human action”.   In keeping with these management policies, the National Park Service maintains its land in the Long Pond watershed in a virtually undeveloped state.  Due to its ownership by the US Government, local land use zoning is not applicable on National Park Service land.

In addition to the undeveloped land owned by the National Park Service, the Town of Southwest Harbor owns several moderately sized undeveloped lots in the watershed to the west of the pond.  Figure 2 shows the land owned by the National Park Service and Town of Southwest Harbor in the Long Pond watershed.

While the south and west portion of the watershed lies within Acadia National Park and is maintained as undeveloped land, most of the land in the eastern and northern portions of the watershed is privately owned.  Land along Ripples Road and Beech Hill Road, at the eastern edge of the watershed is used for a combination of farming and low density residential uses.  Land in the northern part of the watershed, between Round Pond and Oak Hill Cross Road is currently undeveloped woodland.  The northern shoreline of Long Pond and the shoreline of Northern Neck Island in Long Pond are developed with moderate- to high-density seasonal and year round residences.  Residential development density along the eastern shoreline is somewhat less than in the north.  Residential development in the Long Pond watershed relies on private wells and on-site subsurface wastewater disposal systems.

There are several road segments that cross through the Long Pond watershed.  The busiest road is Pretty Marsh Road (Route 102), which passes along the northern edge of Long Pond and provides access to Seal Cove and Tremont at the western edge of Mount Desert Island.  In addition to the primary state and town roads, there is a network of gravel roads that provides access to homes and camps along the shoreline.

The Long Pond watershed is primarily forested with stands of deciduous, evergreen and mixed timber.  Woody and herbaceous wetlands occupy approximately two percent of the watershed.  Developed land uses (e.g., residential, commercial, etc.) occupy less than one percent of the watershed.  A map of the land use classifications for the watershed and surrounding area is shown in Figure 3.

Most recreational activities are permitted on the majority of Long Pond.  Jet skis are prohibited on the pond, however motorized boats are permitted and were observed at both the north and south ends of the pond during the SWAP visit.  Swimming and water contact recreation is prohibited within one mile of the Water Department intake at the south end of the pond.  The swimming prohibition is enforced by the National Park Service rangers.  Ice fishing is permitted on the entire pond.  The Town of Southwest Harbor prohibits road-registered vehicles from the ice at the southern end of the pond.  Vehicles are permitted on the ice in the northern end of the pond, within the Town of Mount Desert.

3.0   INVENTORY OF POTENTIAL WATER QUALITY CONCERNS

### 3.1   Background

### The Source Water Assessment Program (SWAP) is intended to assist water companies and departments in protecting the quality of their surface water supply by identifying potential threats to water quality.  Two factors have been considered in identifying and assessing the potential risk posed by a threat: (a) location in relation to the intake and (b) the nature of a potential threat.

This SWAP assessment looks for potential threats to water quality in three zones:

- The intake zone within 1,000 feet of the intake;

- The shoreline zone, within 250 feet of the shoreline of the surface water body; and,

- The watershed zone, extending to the limits of the surface watershed.

Activities in each of these zones have a different potential effect on the quality of water in the surface supply.

Within each of the three zones, the SWAP assessment examined a variety of conditions, land uses and practices that have a potential to influence water quality.  These features generally fall into one of the following categories:

- Physical characteristics of the watershed, for example the presence of wetlands, steep topography or erodible soils;

- General land uses and development patterns, for example the percentage of developed versus undeveloped land and controls to guide future development; and,

- Specific activities that involve chemical handling or may release pathogens (e.g., fecal coliform) with the potential to degrade water quality.

The SWAP assessment also considered available water quality data from the surface supply as an indicator of existing conditions.  Appendix A describes specific guidance used during the SWAP to inventory potential factors influencing water quality.  Appendix A also lists specific activities included in the SWAP assessment.  Table 2 lists general sources of information consulted during SWAP research.

# TABLE  2

SOURCES OF SWAP INFORMATION

| Information Type | Information Source |
| --- | --- |
| Watershed Characteristics | US Geological Survey (Topography, Hydrology), Soil Conservation Service (Soils), Maine Geological Survey (Geology) |
| Raw Water Quality | Water Department Monitoring, National Park Service Monitoring Data |
| Potential Contamination Sources | DEP Databases and Water Department |
| Land Use and Zoning | Water Department and Municipal Records |
| Other Analyses | Other DEP Databases |

3.2  Source Sensitivity to Land Use

The key watershed features that define the sensitivity of the water supply source to land uses are briefly described below:

- Natural Features:   The watershed is forested and a significant portion is managed by the National Park Service to preserve the natural habitat.  Much of the southern end of the watershed has steep alpine terrain with rock outcrops or thin soil cover.  The pond is deep with a large volume of water in storage.

- Man-made Features:   There is a moderate- to high-density residential community at the north end of the pond, including homes on Northern Neck Island.  There are several roadways that cross through the watershed.  With the exception of Pretty Marsh Road, which carries traffic to the western edge of Mount Desert Island, most roads carry only local traffic.

- Specific Activities:   The presence of shorefront houses and a boat launch at the northern end of the pond encourages a variety of recreational activities on the pond.  These activities are more concentrated at the northern end of the pond, however boating and ice fishing do occur at the southern end of the pond near the Water Department intake.

4.0   ASSESSMENT OF LONG POND

The Long Pond water supply of the Southwest Harbor Water Department is a filtered and chlorinated water supply source.   Based on available data and discussions with the Water Department staff, the drinking water quality derived from the pond has historically been good.

4.1   Watershed

The Long Pond watershed encompasses 4,305 acres of generally alpine terrain.  The surrounding land includes mixed forests on steep slopes, bedrock outcroppings and moderately sloping woods and fields.  Wetlands, one small pond (Round Pond) and several intermittent streams drain into the pond.  Water flows out of Long Pond into Ripple Pond near its north end and then into Somes Pond before flowing to Somes Sound.

Approximately half of the Long Pond watershed is owned by the US Government or the Town of Southwest Harbor and managed to preserve the natural environment.  The Park Service tightly controls and regularly monitors activities in the park, including areas under its control in the Long Pond watershed.  The Water Department relies on the Park Service to patrol the watershed and enforce swimming restrictions at the southern end of the pond.

Private land ownership at the south end of the pond, near the Water Department intake, is limited to a few small residential lots.  The western and northern sides of the watershed consist primarily of privately owned land within the Town of Mount Desert.  Development of seasonal (and some year-round) residences at the north end of the pond and on Northern Neck Island is quite dense.  Residential development in the eastern part of the watershed is less dense than in the north.  According to the Mount Desert codes enforcement officer, approximately a dozen of the homes on the pond are occupied on a year-round basis.  Land near the north and east edges of the watershed is either undeveloped woodlands or developed with low density residential and farm uses.

There are several roadways in the watershed.  The most heavily traveled road is Pretty Marsh Road (Route 102), which passes along the northern end of the pond and is the primary travel route to Seal Cove, Tremont and other areas at the western edge of Mount Desert Island.  Ripples Road and Beech Hill Road form the eastern edge of the watershed and are dead-end roads that carry local traffic.  A number of gravel roads are present in the watershed.  These roads carry local traffic from the primary paved roads to homes on the east and north sides of Long Pond.

Review of the DEP databases of regulated activities and observations made during our reconnaissance of the watershed did not identify other regulated non-residential activities that pose a potential threat to water quality in Long Pond.  The former Southwest Harbor landfill and current transfer station is located approximately 1,500 feet south of the intake.  However, this facility is outside the Long Pond watershed, with drainage flowing southward toward Somes Sound.

4.2   Shoreland

The majority of the western and southern shoreline of Long Pond is undeveloped, with the exception of two houses located approximately 1,000 feet east of the intake.  The National Park Service also maintains a primitive boat launch at the south end of Long Pond (see Figure 2).  A second boat launch is located at the north end of the pond and is maintained by the Town of Mount Desert.

The eastern and northern shoreline, including the shore of Northern Neck, is developed with moderate- to high-density seasonal homes.  The Town of Mount Desert currently zones land along the northern shore as Shoreline Residential 2 (SR2) and requires a 2-acre lot size and 75- foot setback from the pond for new development.  Mount Desert has zoned the land along the eastern shore as SR5, requiring 5-acre lots and a 75-foot setback from the pond.  According to the Code Enforcement Officer, it is increasingly common for owners to convert existing seasonal homes on the pond to year-round homes, including those on small lots that do not meet the current size requirements.  The town recognizes that inadequate septic systems could pose a threat to the quality of Long Pond and has instituted a program for landowners offering pumping and inspection of systems every four years.

Pretty Marsh Road, the busiest road in the watershed, passes within 250 feet of the pond at its northern end.  This road also provides access to the Mount Desert boat launch and residential properties along the north end of the pond.

Forest cover in the southern and western parts of the watershed generally extends down to the shoreline.  The associated vegetative growth stabilizes soil and minimizes erosion.  Activities associated with the development along the eastern and northern shore (e.g., gravel roads), as well as the characteristics of the native soil, pose a potential threat to water quality from soil erosion.  Figure 4 is a map of potentially erodible soils along the Long Pond shoreline.  While there is

some potential for soil erosion, the Water Department reports minimal turbidity increases that would be attributable to erosion following storm events.

4.3   Intake

The water supply intake is located at the south end of the pond, at a depth of approximately 10 feet.  At the intake, the pond is approximately 80 feet deep.  The intake is not marked with signs or buoys.  The outlet to the pond is located at the northern end of the pond, more than three miles north of the intake.  The natural flow conditions from south to north in the pond would be expected to buffer water quality at the intake from activities that occur at the northern end of the pond.

Water contact activities, such as swimming, are prohibited within one mile of the intake, which encompasses the southern one-third of the pond.  Signs are posted at the Water Department pump station and at the Park Service boat launch alerting visitors to this restriction.  Park Service rangers enforce the no swimming restriction according to Water Department staff.

Other recreational activities, including boating using outboard engines and fishing, are permitted on all parts of the pond.  Jet skis have been prohibited on all of Long Pond.  A float plane was moored near the northern boat launch at the time of our visit.  According to Water Department staff, the plane fuels at a nearby airport, rather than on the pond.

Winter recreation on Long Pond includes ice fishing and snowmobiling.   The Town of Southwest Harbor has enacted a prohibition preventing road-registered vehicles from driving on the ice at the south end of the pond.  However, vehicles are permitted on the Mount Desert end of the pond.

Lakes and ponds normally experience an aging process known as eutrophication, which is caused by various natural and man-made influences.   Phosphorus from runoff, fertilizers, sewage and other sources is a primary factor affecting eutrophication since phosphorus nourishes plant and algae growth in the pond.   The amount of algae productivity in the pond is characterized using three Trophic States: (1) Oligotrophic = low, (2) Mesotrophic = moderate, and (3) Eutrophic = high.  The Trophic State can be identified based on chlorophyll-a and phosphorus content and by secchi disk transparency data, which measures the clarity of the pond water.

The National Park Service has monitored water quality in many of the ponds in Acadia National Park, including Long Pond, since 1981.  Summary data reviewed for this SWAP report showed that secchi disk transparency was stable through the period at approximately 7 to 10 meters.  Measurements of chlorophyll-a during 1981, 1984 and 1995 showed concentrations of 1 to 3 parts per billion (ppb).  The concentration of total phosphorous has exhibited a fairly wide range over the period with average concentration as low as 3 ppb and as high as 12.5 ppb.  The Park Service data show that Long Pond is well oxygenated throughout its depth.

According to a surface water classification database developed by the DEP, the Trophic State of Long Pond is listed as Oligotrophic.  The pond water is ranked as fully attaining the GPA classification for all criteria.   Based on all the testing completed to date on the raw water from Long Pond, the water is a high quality source.

5.0   SWAP RANKING AND RECOMMENDATIONS

5.1   Ranking of Susceptibility

The SWAP assessment factors indicate that overall susceptibility of the water quality in Long Pond is low.  This conclusion is based on the general conditions observed, including the size of the pond, the strict limits on development on Park Service land and the relationship of developed areas to the water supply intake.  Specific factors considered in assessing the overall risk are summarized in Table 3.

# TABLE  3

# LONG POND SURFACE WATER ASSESSMENT

| Zone | Measure | Findings | Risk Level |
| --- | --- | --- | --- |
| Watershed | Ambient Water Quality Existing Conditions Future Development Overall | Class GPA, in full compliance. The half of the watershed nearest the intake is undeveloped and managed for natural conditions. Developed areas near the outfall include low to high-density residential development. Park Service management policy prevents future development. Zoning restricts future development on private land to 2 acres or greater. | Low Low-Moderate Low Low |
| Shoreland | Pond Classification Soils Activities Posing a Threat Potential for Future Threats Overall | Oligotrophic Erodible soils are most common along the northern shoreline near the outfall but are less common to the south. Activities are strictly limited near the intake in the south. There are few restrictions on shorefront activities in the north. There is general pressure to convert shorefront homes for year-round use. | Low Low Low-Moderate Low Low |
| Intake | Raw Water Quality Ownership/Control Activities Posing a Threat Potential for Future Threats Overall | Analytical data show high water quality. Intake area controlled by Park Service. There are few restrictions on recreational access to the intake area via boats. There is a general trend in the area toward increasing recreational use. | Low Low Low-Moderate Low-Moderate Low-Moderate |
| Overall |  |  | Low |

5.2   Recommendations

The overall ranking for the pond susceptibility to threats of contamination is low.  Long Pond is long and deep and the water supply intake is located at the southern end of the pond.  Current land use around the intake is almost entirely undeveloped and future development is precluded by National Park Service control.  Possible threats to the overall water quality of the pond are related to recreational uses and development at the north end of the pond, near the outfall. Several actions could be considered by the Water Department, the towns of Southwest Harbor and Mount Desert and the Park Service to provide added protection to the quality of the water supply.

- The most direct and least restricted access to the pond near the intake is via boat.  The Water Department may want to work with the towns and the Park Service to pursue additional safeguards to limit access to the portion of the pond nearest the intake.  This could take the form of a buoyed zone around the intake or a wider area with limitations on boating activities (e.g., horsepower restrictions).

- Existing residential development at the northern end of the pond encourages recreation on both the north and south ends of the pond.  The Water Department should consider educational outreach to shorefront homeowners to inform them of the water supply intake at the south end of the pond and solicit their support for water quality protection.

- Similarly, existing residential development at the north end of the pond includes a network of gravel roads and reliance on septic systems for wastewater disposal.  Soil erosion along roads and poorly functioning septic systems pose threats to the water quality of Long Pond.  The Water Department should consider working with Mount Desert officials and homeowner groups to monitor and improve on activities that could pose water quality threats.

- Pretty Marsh Road passes close to the shoreline of Long Pond.  There are other gravel roads that also pass along the shoreline to provide access to private homes.  The Water Department should consider working with the Southwest Harbor and Mount Desert public works departments and the National Park Service to develop a contingency plan to respond to vehicle accidents along the shoreline of Long Pond.

- The Water Company, Park Service and other groups (e.g., the WRI) should continue monitoring water quality in Long Pond.  These data should be reviewed regularly for signs that water quality is deteriorating (e.g., trend of increasing concentrations of nutrients, etc.).

#### APPENDIX A

SWAP ASSESSMENT GUIDELINES

MAINE PUBLIC DRINKING WATER

SOURCE WATER ASSESSMENT PROGRAM

SOUTHWEST HARBOR WATER DEPARTMENT

LONG POND WATERSHED

# APPENDIX A

# ASSESSMENT GUIDELINES

| Assessment Item/Threat | Low | Moderate | Significant |
| --- | --- | --- | --- |
| Physical Characteristics of the Watershed Watershed boundary, area Area of water body Tributaries Watershed topography Wetlands Water body depth Sand and gravel aquifers Soil types (erodibility and slope) | Smaller Smaller Few Low Many Deep Few Low | >> >> >> moderate >> >> some moderate | larger larger many steep, rugged few shallow many high |
| Raw Water Quality Secchi Disk Transparency Turbidity pH Phosphorus Pesticides and herbicides Color Total Coliform and E Coli Dissolved Oxygen Temperature VOCs Chlorophyll-a Total Organic Carbon | > 8 M < 1 NTU 6.5-8.5 < 10 ppb ND < 5 > 29/100 ml >7 mg/L ambient absent < 2 ppb < 4 mg/L | 4-8 M < 5 NTU N/A < 20 ppb N/A 5-15 occasional 5-7 mg/L N/A 2-6 ppb 4-8 mg/L | < 4 M > 5 NTU < 6.5 or > 8.5 > 30 ppb detected > 15 > 142/100 ml < 5 mg/L > 10o C ambient detected > 6 ppb > 8 mg/L |
| Potential Contamination Source Inventory UST/AST leak sites Municipal/Comm/Special Landfill Compost sites Demolition debris sites Ash/septage storage/utilization Superfund site Sand/salt storage sites Petroleum spill sites Hazardous waste sites Wastewater treatment facilities Food residuals utilization sites Uncontrolled hazardous sites Tank farms Industrial complexes | Absent from Watershed or Actively monitored and controlled or fully remediated. | Present in watershed, some operational deficiencies and/or remediation is underway. | Present and unmonitored and/or unremediated. |

| Assessment Item/Threat | Low | Moderate | Significant |
| --- | --- | --- | --- |
| Potential Contamination Source Inventory Non-point pollution sources Transfer stations Sludge utilization sites Automobile graveyards Engineered subsurface systems Woodyards Underground injection wells Surface impoundments Mining/mineral processing sites Overboard discharges to rivers Active UST sites Roadways Railroads Utility Rights-of-way Boat launches Commercial farms CAFOs Commercial forest operations Private septic systems Home heating oil tanks Airports Bathing beaches Combined sewage overflows | If present, at low density, properly installed and operated. In compliance with applicable local, state and federal regulations. | >>>> | High density, little evidence of active management, documented incidence of problems and failures. |
| Land Uses and Zoning Residential density Percent of watershed Owned by PWS Public lands or conservation Forested With protective zoning Agricultural Impervious cover Industrial/commercial Water body uses: Restricted areas Ice fishing Boating Swimming Recreational vehicles | > 2 Ac/lot total > 80% for all protected uses < 20 % total < 20 % total < 20 % total large, posted limited to absent | 1-2 Ac/lot intake and shoreland protected, others developed 20-30% total 20-30% total 20-30% total intake zone moderate, well-managed | < 1 Ac/lot critical areas (intake, shoreland) unprotected or developed > 30% total of 3 > 30% total of 3 > 30% total of 3 small to none prevalent, uncontrolled |
| Other Analyses Trophic State Index Vulnerability Index Build-out Analysis | < 25 low fully developed | 25-60 moderate >>> | > 60 high high potential for development |